# ТЕХНИЧЕСКОЕ ЗАДАНИЕ

## Линия А - система получения очищенной воды для ИФА-производства (50 л/час)

### 1. Назначение

Система предназначена для получения очищенной воды, используемой при производстве диагностических ИФА-наборов, приготовлении буферных и промывочных растворов, технологических операциях лабораторно-производственного цикла, а также для обеспечения вспомогательных производственных процессов.

Система должна обеспечивать разделение потоков воды на:

- производственную линию очищенной воды;

- техническую линию хозяйственно-вспомогательного назначения.

# 2. Требуемая производительность

Производительность готовой очищенной воды:

- не менее 50 л/час.

Объем накопительной емкости:

- 300–500 л.

# 3. Область применения

## Производственная линия очищенной воды

Используется для:

- приготовления фосфатно-солевых буферов;

- приготовления рабочих буферных растворов;

- приготовления промывочных растворов;

- приготовления реагентов ИФА-наборов;

- технологических операций при производстве ИФА;

- подачи очищенной воды непосредственно в миксер-танк.

## Техническая линия

Используется для:

- мойки лабораторной посуды;

- предварительной мойки оборудования;

- санитарно-хозяйственных нужд;

- вспомогательных технологических операций.

# 4. Состав линии

Система должна включать:

- Фильтр механической очистки.

- Угольный фильтр.

- Систему умягчения воды.

- Систему дозирования антискаланта.

- Установку обратного осмоса RO (желательно двухступенчатую).

- Ультрафиолетовый стерилизатор UV 254 нм.

- Финишный фильтр 0,22 мкм.

- Накопительную емкость очищенной воды объемом 300–500 л.

- Насосную группу подачи очищенной воды.

- Систему автоматической промывки мембран.

- Онлайн-контроль проводимости воды.

- Контроль давления до и после фильтров.

- PLC/HMI шкаф управления либо аналогичную автоматизированную систему управления.

- Производственную линию подачи очищенной воды из нержавеющей стали SS304, предпочтительно SS316L.

- Отдельную техническую линию подачи воды для хозяйственно-вспомогательных нужд.

- Санитарные точки отбора проб воды:

- после установки обратного осмоса;

- после UV-стерилизатора;

- после финишного фильтра 0,22 мкм;

- перед подачей в миксер-танк.

- Дренажную систему отвода концентрата и промывочных вод.

# 5. Основные требования

- Материал контактирующих частей: SS304, предпочтительно SS316L.

- Производственная линия подачи очищенной воды должна быть выполнена отдельно от общего пластикового трубопровода.

- Подача воды, предназначенной для приготовления буферных растворов и реагентов ИФА, через общий пластиковый трубопровод не допускается.

- Производственная линия должна обеспечивать прямую подачу очищенной воды в миксер-танк.

- Техническая линия допускается из пищевого пластикового трубопровода.

- Автоматический режим работы системы.

- Защита насосов от сухого хода.

- Возможность санитарной обработки системы.

- Наличие автоматической промывки мембран.

- Возможность подключения линии ультрачистой воды в будущем.

- Возможность непрерывной эксплуатации.

- Наличие аварийной сигнализации при превышении проводимости.

# 6. Требования к качеству воды

Ориентировочные показатели очищенной воды:

- проводимость: желательно не более 10–20 µS/cm;

- отсутствие механических примесей;

- отсутствие запаха;

- отсутствие окраски;

- стабильность качества воды при непрерывной эксплуатации;

- снижение микробной контаминации за счет UV-обеззараживания и финишной фильтрации.

Контроль качества воды должен проводиться:

- после установки обратного осмоса;

- после UV-стерилизатора;

- после финишного фильтра 0,22 мкм;

- перед подачей воды в миксер-танк.

# 7. Требования к монтажу

- Поставщик должен предусмотреть подключение системы к скважинной воде.

- Производственная линия должна иметь минимальное количество тупиковых участков.

- Трубопроводы производственной линии должны быть выполнены с возможностью санитарной обработки.

- Все соединения производственной линии должны быть герметичными и пригодными для эксплуатации в пищевой/фармацевтической промышленности.

# 8. Документация от поставщика

Поставщик обязан предоставить:

- коммерческое предложение;

- техническую спецификацию;

- технологическую схему системы;

- схему трубопроводов;

- электрическую схему;

- паспорт оборудования;

- руководство по эксплуатации;

- перечень расходных материалов;

- график замены фильтров и мембран;

- гарантийные условия;

- фото и/или видео аналогичных реализованных установок;

- перечень сервисного обслуживания;

- требования к помещению и коммуникациям.

# 9. Гарантийные требования

- Гарантийный срок: не менее 12 месяцев.

- Наличие сервисной поддержки.

- Возможность поставки расходных материалов и мембран на территории Республики Казахстан.

# TECHNICAL SPECIFICATION

## Line A - Purified Water Generation System for ELISA Production (50 L/hour)

### 1. Purpose

The system is intended for the production of purified water used in the manufacturing of diagnostic ELISA kits, preparation of buffer and washing solutions, laboratory-production technological processes, and support of auxiliary production operations.

The system shall provide separation of water flows into:

- a production purified water line;

- a technical/service water line.

# 2. Required Capacity

Purified water production capacity:

- not less than 50 L/hour.

Storage tank volume:

- 300–500 L.

# 3. Scope of Application

## Production Purified Water Line

Used for:

- preparation of phosphate-buffered saline (PBS) and other buffer solutions;

- preparation of working buffer solutions;

- preparation of washing solutions;

- preparation of ELISA kit reagents;

- technological operations during ELISA kit manufacturing;

- direct supply of purified water to the mixing tank.

## Technical Water Line

Used for:

- washing laboratory glassware;

- preliminary washing of equipment;

- sanitary and utility purposes;

- auxiliary technological operations.

# 4. System Configuration

The system shall include:

- Mechanical pre-filter.

- Activated carbon filter.

- Water softening system.

- Antiscalant dosing system.

- Reverse osmosis (RO) unit, preferably double-stage.

- UV sterilizer, 254 nm.

- Final filter, 0.22 µm.

- Purified water storage tank, 300–500 L.

- Pumping unit for purified water supply.

- Automatic membrane flushing system.

- Online conductivity monitoring system.

- Pressure monitoring before and after filters.

- PLC/HMI control cabinet or equivalent automated control system.

- Production purified water pipeline made of SS304 stainless steel, preferably SS316L.

- Separate technical water pipeline for utility and auxiliary needs.

- Sanitary sampling points:

- after the reverse osmosis unit;

- after the UV sterilizer;

- after the 0.22 µm final filter;

- before water supply to the mixing tank.

- Drainage system for concentrate and flushing water disposal.

# 5. Main Requirements

- Material of all wetted/contact parts: SS304 stainless steel, preferably SS316L.

- The production purified water pipeline shall be completely separated from the general plastic piping system.

- Water intended for preparation of ELISA buffers and reagents shall not be supplied through the common plastic pipeline.

- The production line shall provide direct purified water supply to the mixing tank.

- The technical water line may be made of food-grade plastic piping.

- Fully automatic operation mode.

- Dry-run protection for pumps.

- Capability for sanitary cleaning/sanitization of the system.

- Automatic membrane flushing function.

- Capability for future connection to an ultrapure water system.

- Capability for continuous operation.

- Alarm system for excessive conductivity levels.

# 6. Water Quality Requirements

Indicative purified water parameters:

- conductivity: preferably not more than 10–20 µS/cm;

- absence of mechanical impurities;

- absence of odor;

- absence of color;

- stable water quality during continuous operation;

- reduction of microbial contamination through UV sterilization and final filtration.

Water quality monitoring shall be performed:

- after the reverse osmosis unit;

- after the UV sterilizer;

- after the 0.22 µm final filter;

- before water supply to the mixing tank.

# 7. Installation Requirements

- The supplier shall provide connection of the system to well water supply.

- The production purified water pipeline shall have a minimal number of dead legs.

- The production piping shall be designed for sanitary cleaning/sanitization.

- All production line connections shall be leak-tight and suitable for food/pharmaceutical industry applications.

# 8. Documentation to Be Provided by Supplier

The supplier shall provide:

- commercial quotation;

- technical specification;

- process flow diagram;

- piping diagram;

- electrical diagram;

- equipment passport/data sheet;

- operation and maintenance manual;

- list of consumables;

- schedule for replacement of filters and membranes;

- warranty conditions;

- photos and/or videos of similar installed systems;

- service maintenance requirements;

- utility and room requirements.

# 9. Warranty Requirements

- Warranty period: minimum 12 months.

- Availability of technical/service support.

- Availability of consumables and membrane supply within the Republic of Kazakhstan.